BHI Model: 916U

How to Order: Model + Heater Code with color code + Options (example 916U00875CW-1500-T1)

| Length In. (mm) | Density |  | Watts | Heater Code |  |  |  |  |  |  |  |  | Watts at 240/208V | Heater Code |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | W/Ft | W/m |  |  | 208V | Amps |  | 277V | Amps |  | 480V | Amps |  |  | 240/208V | Amps |
| 23.6 (600) | 175 | 575 | 375 |  | 00375C‡-600 | 1.8 |  | 00375N‡-600 | 1.4 |  | — | — | 375/281 |  | 00375V‡-600 | 1.6/1.4 |
|  | 250 | 820 | 500 |  | 00500C‡-600 | 2.4 |  | 00500N‡-600 | 1.8 |  | — | — | 500/375 |  | 00500V‡-600 | 2.1/1.8 |
|  | 355 | 1165 | 750 |  | 00750C‡ | 3.6 |  | 00750N‡ | 2.7 |  | — | — | 750/563 |  | 00500V‡ | 3.1/2.7 |
|  | 500 | 1640 | 1000 |  | 01000C‡-600 | 4.8 |  | 01000N‡-600 | 3.6 |  | 01000T‡-600 | 2.1 | 1000/750 |  | 01000V‡-600 | 4.2/3.6 |
| 35.4 (900) | 175 | 575 | 500 |  | 00500C‡-900 | 2.4 |  | 00500N‡-900 | 1.8 |  | 00500T‡-900 | 1 | 500/375 |  | 00500V‡-900 | 2.1/1.8 |
|  | 250 | 820 | 750 |  | 00750C‡-900 | 3.6 |  | 00750N‡-900 | 2.7 |  | 00750T‡-900 | 1.6 | 750/563 |  | 00750V‡-900 | 3.1/2.7 |
|  | 355 | 1165 | 1000 |  | 01000C‡ | 4.8 |  | 01000N‡ | 3.6 |  | 01000T‡ | 2.1 | 1000/751 |  | 01000V‡ | 4.2/3.6 |
|  | 500 | 1640 | 1500 |  | 01500C‡-900 | 7.2 |  | 01500N‡-900 | 5.4 |  | 01500T‡-900 | 3.1 | 1500/1125 |  | 01500V‡-900 | 6.3/5.4 |
| 47.3 (1200) | 175 | 575 | 700 |  | 00700C‡-1200 | 3.4 |  | 00700N‡-1200 | 2.5 |  | 00700T‡-1200 | 1.5 | 700/525 |  | 00700V‡-1200 | 2.9/2.5 |
|  | 250 | 820 | 1000 |  | 01000C‡-1200 | 4.8 |  | 01000N‡-1200 | 3.6 |  | 01000T‡-1200 | 2.1 | 1000/750 |  | 01000V‡-1200 | 4.2/3.6 |
|  | 355 | 1165 | 1400 |  | 01400C‡ | 6.7 |  | 01400N‡ | 5.1 |  | 01400T‡ | 2.9 | 1400/1052 |  | 01400V‡ | 5.8/5.1 |
|  | 500 | 1640 | 2000 |  | 02000C‡-1200 | 9.6 |  | 02000N‡-1200 | 7.2 |  | 02000T‡-1200 | 4.2 | 2000/1500 |  | 02000V‡-1200 | 8.3/7.2 |
| 59.1 (1500) | 175 | 575 | 875 |  | 00875C‡-1500 | 4.2 |  | 00875N‡-1500 | 3.2 |  | 00875T‡-1500 | 1.8 | 875/656 |  | 00875V‡-1500 | 3.6/3.2 |
|  | 250 | 820 | 1250 |  | 01250C‡-1500 | 6 |  | 01250N‡-1500 | 4.5 |  | 01250T‡-1500 | 2.6 | 1250/938 |  | 01250V‡-1500 | 5.2/4.5 |
|  | 355 | 1165 | 1750 |  | 01750C‡ | 8.4 |  | 01750N‡ | 6.3 |  | 01750T‡ | 3.6 | 1750/1314 |  | 01750V‡ | 7.3/6.3 |
|  | 500 | 1640 | 2500 |  | 02500C‡-1500 | 12 |  | 02500N‡-1500 | 9 |  | 02500T‡-1500 | 5.2 | 2500/1875 |  | 02500V‡-1500 | 10.4/9.0 |
| 70.9 (1800) | 175 | 575 | 1050 |  | 01050C‡-1800 | 5 |  | 01050N‡-1800 | 3.8 |  | 01050T‡-1800 | 2.2 | 1050/788 |  | 01050V‡-1800 | 4.4/3.8 |
|  | 250 | 820 | 1500 |  | 01500C‡-1800 | 7.2 |  | 01500N‡-1800 | 5.4 |  | 01500T‡-1800 | 3.1 | 1500/1125 |  | 01500V‡-1800 | 6.3/5.4 |
|  | 355 | 1165 | 2100 |  | 02100C‡ | 10.1 |  | 02100N‡ | 7.6 |  | 02100T‡ | 4.4 | 2100/1577 |  | 02100V‡ | 8.8/7.6 |
|  | 500 | 1640 | 3000 |  | 03000C‡-1800 | 14.4 |  | 03000N‡-1800 | 10.8 |  | 03000T‡-1800 | 6.3 | 3000/2250 |  | 03000V‡-1800 | 12.5/10.8 |
| 82.7 (2100) | 175 | 575 | 1225 |  | 01225C‡-2100 | 5.9 |  | 01225N‡-2100 | 4.4 |  | 01225T‡-2100 | 2.6 | 1225/919 |  | 01225V‡-2100 | 5.1/4.4 |
|  | 250 | 820 | 1750 |  | 01750C‡-2100 | 8.4 |  | 01750N‡-2100 | 6.3 |  | 01750T‡-2100 | 3.6 | 1750/1313 |  | 01750V‡-2100 | 7.3/6.3 |
|  | 355 | 1165 | 2450 |  | 02450C‡ | 11.8 |  | 02450N‡ | 8.8 |  | 02450T‡ | 5.1 | 2450/1840 |  | 02450V‡ | 10.2/8.8 |
|  | 500 | 1640 | 3500 |  | 03500C‡-2100 | 16.8 |  | 03500N‡-2100 | 12.6 |  | 03500T‡-2100 | 7.3 | 3500/2625 |  | 03500V‡-2100 | 14.6/12.6 |
| 94.5 (2400) | 175 | 575 | 1400 |  | 01400C‡-2400 | 6.7 |  | 01400N‡-2400 | 5.1 |  | 01400T‡-2400 | 2.9 | 1400/1050 |  | 01400V‡-2400 | 5.8/5.0 |
|  | 250 | 820 | 2000 |  | 02000C‡-2400 | 9.6 |  | 02000N‡-2400 | 7.2 |  | 02000T‡-2400 | 4.2 | 2000/1500 |  | 02000V‡-2400 | 8.3/7.2 |
|  | 355 | 1165 | 2800 |  | 02800C‡ | 13.5 |  | 02800N‡ | 10.1 |  | 02800T‡ | 5.8 | 2800/2103 |  | 02800V‡ | 11.7/10.1 |
|  | 500 | 1640 | 4000 |  | 04000C‡-2400 | 19.2 |  | 04000N‡-2400 | 14.4 |  | 04000T‡-2400 | 8.3 | 4000/3000 |  | 04000V‡-2400 | 16.7/14.4 |

Other single-phase voltages available, consult factory. All models are single-phase.

‡ Standard colors - Add W for white finish or A for almond finish to the end of catalog number when ‡ is indicated.

Factory Built-in Options

| Code | Description |  |
| --- | --- | --- |
| D1 | Disconnect Switch, Three-pole, 600V, 40 Amp |  |
| D3 | Disconnect Switch, Double-pole, 277V, 20 Amp |  |
| F1 | 24V Wireway |  |
| L | Custom Length |  |
| M1 | High Altitude Automatic Cutout |  |
| R1 | 24V Relay, 240V, 22 Amp; 277V, 19 Amp |  |
| R2 | 24V Relay with Transformer, 240V, 22 Amp; 277V, 19 Amp |  |
| R6 | Pneumatic Relay, 480V, 25 Amp |  |
| R7 | 24V Proportional Relay |  |
| S | Smooth Finish on Heater Back |  |
| T1 | Tamperproof Thermostat, Single-pole, 240V, 25 Amp; 600V, 10 Amp |  |
| T2 | Tamperproof Thermostat, Double-pole, 240V, 30 Amp; 600V, 15 Amp |  |
| T5 | Adjustable Thermostat, Single-Pole 240V, 25 Amp, 600V, 10 Amp |  |
| T6 | Adjustable Thermostat, Double-Pole 240V, 30 Amp, 600V, 15 Amp |  |

Architect’s and Engineers Specifications

Heating Elements – Two stainless steel elements with aluminum fins float on high temperature nylon bushings for quiet operation.

Housing – Cabinet is constructed of 18-gauge steel with a 14-gauge aluminum front and top covers.  The unit has a polyester powder paint finish in white or almond.  End caps are provided on all units.

Inlet/Outlet Grilles – The fresh air inlet is located on the bottom of the unit.  The top outlet grille has openings less than 0.25 inches to discourage tampering with the heating element (pencil-proof).

Built-in Controls – Linear limit, automatic reset thermal cutout.

Electrical Connection – Each heater has a junction box located at the right end and a built-in full length wireway. Seprate low voltage wireway is available.

Installation Requirements – Minimum installation height above the floor is three inches.  Field or factory-installed low voltage relay and thermostat kits fit into the right-hand junction box only. These units are not for residential use in the United States.

Field-Installed Options

(shipped loose for field installation into heater)

| Catalog Number | Description |  |
| --- | --- | --- |
| 916-166753¶ | Inside Corner |  |
| 916-166754¶ | Outside Corner |  |
| 916-166756¶ | Square Pedestal Kit, 3”, Qty=2 |  |
| 916-166757¶ | Splice Plate 2” Long |  |
| 916-166758¶ | Finish Joint for Heater with Pedestal |  |
| 916-166759 | 24V Relay Kit, 240V, 22 Amp; 277V, 19 Amp |  |
| 916-166760 | 24V Relay Kit with Transformer, 208V, 22 Amp |  |
| 916-166761 | 24V Relay Kit with Transformer, 240V, 22 Amp |  |
| 916-166762 | 24V Relay Kit with Transformer, 277V, 19 Amp |  |
| 916B-XXX¶ | Blank Section (specify length in inches-XXX) |  |
| 916-224765 | Tamperproof Thermostat, Single-pole, 240V, 25 Amp; 600V, 10 Amp |  |
| 916-224766 | Tamperproof Thermostat, Double-pole, 240V, 30 Amp; 600V, 15 Amp |  |
| 916-264350 | Adjustable Thermostat, Single-Pole 240V, 25 Amp, 600V, 10 Amp with off position |  |
| 916-264351 | Adjustable Thermostat, Double-Pole 240V, 30 Amp, 600V, 15 Amp with off position |  |

¶ Standard colors - Add W for white finish or A for almond finish to the end of part number.