|  | Built-in digital thermostat with timer is included. Watts Volts Amps Weight lb (kg) Catalog Number 1500 120 12.5 22.8 (10.3) 940U01500B¶ 2000 240 8.3 22.8 (10.3) 940U02000J¶ ¶Standard colors – Add W for white finish or A for almond finish to the end of catalog number. Factory Built-in Options Code Description D3 Disconnect Switch, 277V, Double-pole, 20 Amp Field-Installed Options Catalog Number Description 940-213895¶ Cast Aluminum Surface Mounting Box ¶Standard colors – Add W for white finish or A for almond finish to the end of catalog number. |
| --- | --- |

Architect’s and Engineer’s Specifications

Heating Elements – Instant heat nickel-chrome coil resistant wire element.

Outlet Grille – Heavy cast aluminum front cover with steel bar inlet and outlet grilles has a polyester powder paint finish available in white or almond.

Built-in Controls – Digital display electronic thermostat with timer, automatic reset thermal cutout, temperature sensor and LED night light with on-off switch.

Fan motor – Whisper-quiet squirrel-cage fan with factory-lubricated motor.

Installation Requirements –Maintain a minimum of 4-inches (102 mm) clearance below heater, 1-inch (25 mm) to adjacent walls and 48-inches (1219 mm) in front of heater.

Rough In Dimensions – All heaters: 18-5/8” wide x 13-3/8” high x 2-3/4” deep.