| KW | Volts | Phase | Total Amps (1) | CFM | Approximate Air Temperature Rise oF (oC) | Motor Data | Catalog Number |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | HP | RPM | Voltage |  |  |
| 2 | 208 | 1 | 10.3 | 700 | 9 (5) | 1/30 | 1550 | 240/208 | 926U02000CA |  |
|  | 208 | 3 | 6.3 | 700 | 9 (5) | 1/30 | 1550 | 240/208 | 926U02000DA |  |
|  | 240 | 1 | 9.0 | 700 | 9 (5) | 1/30 | 1550 | 240/208 | 926U02000JA |  |
|  | 240 | 3 | 5.5 | 700 | 9 (5) | 1/30 | 1550 | 240/208 | 926U02000KA |  |
|  | 277 | 1 | 7.9 | 700 | 9 (5) | 1/30 | 1550 | 240/208 | 926U02000NA |  |
|  | 480 | 1 | 4.9 | 700 | 9 (5) | 1/30 | 1550 | 240/208 | 926U02000TA |  |
|  | 480 | 3 | 3.1 | 700 | 9 (5) | 1/30 | 1550 | 240/208 | 926U02000UA |  |
| 3 | 208 | 1 | 15.1 | 700 | 14 (8) | 1/30 | 1550 | 240/208 | 926U03000CA |  |
|  | 208 | 3 | 9.0 | 700 | 14 (8) | 1/30 | 1550 | 240/208 | 926U03000DA |  |
|  | 240 | 1 | 13.2 | 700 | 14 (8) | 1/30 | 1550 | 240/208 | 926U03000JA |  |
|  | 240 | 3 | 7.9 | 700 | 14 (8) | 1/30 | 1550 | 240/208 | 926U03000KA |  |
|  | 277 | 1 | 11.5 | 700 | 14 (8) | 1/30 | 1550 | 240/208 | 926U03000NA |  |
|  | 480 | 1 | 7.0 | 700 | 14 (8) | 1/30 | 1550 | 240/208 | 926U03000TA |  |
|  | 480 | 3 | 4.3 | 700 | 14 (8) | 1/30 | 1550 | 240/208 | 926U03000UA |  |
| 4 | 208 | 1 | 19.9 | 700 | 18 (10) | 1/30 | 1550 | 240/208 | 926U04000CA |  |
|  | 208 | 3 | 11.8 | 700 | 18 (10) | 1/30 | 1550 | 240/208 | 926U04000DA |  |
|  | 240 | 1 | 17.4 | 700 | 18 (10) | 1/30 | 1550 | 240/208 | 926U04000JA |  |
|  | 240 | 3 | 10.3 | 700 | 18 (10) | 1/30 | 1550 | 240/208 | 926U04000KA |  |
|  | 277 | 1 | 15.1 | 700 | 18 (10) | 1/30 | 1550 | 240/208 | 926U04000NA |  |
|  | 480 | 1 | 9.0 | 700 | 18 (10) | 1/30 | 1550 | 240/208 | 926U04000TA |  |
|  | 480 | 3 | 5.5 | 700 | 18 (10) | 1/30 | 1550 | 240/208 | 926U04000UA |  |
| 5 | 208 | 1 | 24.7 | 700 | 23 (13) | 1/30 | 1550 | 240/208 | 926U05000CA |  |
|  | 208 | 3 | 14.6 | 700 | 23 (13) | 1/30 | 1550 | 240/208 | 926U05000DA |  |
|  | 240 | 1 | 21.5 | 700 | 23 (13) | 1/30 | 1550 | 240/208 | 926U05000JA |  |
|  | 240 | 3 | 12.7 | 700 | 23 (13) | 1/30 | 1550 | 240/208 | 926U05000KA |  |
|  | 277 | 1 | 18.8 | 700 | 23 (13) | 1/30 | 1550 | 240/208 | 926U05000NA |  |
|  | 480 | 1 | 11.1 | 700 | 23 (13) | 1/30 | 1550 | 240/208 | 926U05000TA |  |
|  | 480 | 3 | 6.7 | 700 | 23 (13) | 1/30 | 1550 | 240/208 | 926U05000UA |  |
| 7.5 | 208 | 1 | 36.8 | 700 | 34 (19) | 1/30 | 1550 | 240/208 | 926U07500CA |  |
|  | 208 | 3 | 21.5 | 700 | 34 (19) | 1/30 | 1550 | 240/208 | 926U07500DA |  |
|  | 240 | 1 | 32.0 | 700 | 34 (19) | 1/30 | 1550 | 240/208 | 926U07500JA |  |
|  | 240 | 3 | 18.7 | 700 | 34 (19) | 1/30 | 1550 | 240/208 | 926U07500KA |  |
|  | 277 | 1 | 27.8 | 700 | 34 (19) | 1/30 | 1550 | 240/208 | 926U07500NA |  |
|  | 480 | 1 | 16.3 | 700 | 34 (19) | 1/30 | 1550 | 240/208 | 926U07500TA |  |
|  | 480 | 3 | 9.7 | 700 | 34 (19) | 1/30 | 1550 | 240/208 | 926U07500UA |  |
| 10 | 208 | 1 | 48.8 | 700 | 45 (25) | 1/30 | 1550 | 240/208 | 926U10000CA (2) |  |
|  | 208 | 3 | 28.5 | 700 | 45 (25) | 1/30 | 1550 | 240/208 | 926U10000DA |  |
|  | 240 | 1 | 42.4 | 700 | 45 (25) | 1/30 | 1550 | 240/208 | 926U10000JA |  |
|  | 240 | 3 | 24.8 | 700 | 45 (25) | 1/30 | 1550 | 240/208 | 926U10000KA |  |
|  | 480 | 1 | 21.5 | 700 | 45 (25) | 1/30 | 1550 | 240/208 | 926U10000TA |  |
|  | 480 | 3 | 12.7 | 700 | 45 (25) | 1/30 | 1550 | 240/208 | 926U10000UA |  |
| 15 | 208 | 1 | 73.2 | 1300 | 36 (20) | 1/8 | 1550 | 240/208 | 926U15000CA |  |
|  | 208 | 3 | 42.7 | 1300 | 36 (20) | 1/8 | 1550 | 240/208 | 926U15000DA |  |
|  | 240 | 1 | 63.6 | 1300 | 36 (20) | 1/8 | 1550 | 240/208 | 926U15000JA |  |
|  | 240 | 3 | 37.2 | 1300 | 36 (20) | 1/8 | 1550 | 240/208 | 926U15000KA |  |
|  | 480 | 1 | 32.2 | 1400 | 34 (19) | 1/6 | 1725 | 480 (1 ph) | 926U15000TA |  |
|  | 480 | 3 | 18.9 | 1400 | 34 (19) | 1/6 | 1725 | 480 (1 ph) | 926U15000UA |  |
| 20 | 208 | 1 | 97.3 | 1300 | 49 (27) | 1/8 | 1550 | 240/208 | 926U20000CA |  |
|  | 208 | 3 | 56.6 | 1300 | 49 (27) | 1/8 | 1550 | 240/208 | 926U20000DA |  |
|  | 240 | 1 | 84.4 | 1300 | 49 (27) | 1/8 | 1550 | 240/208 | 926U20000JA |  |
|  | 240 | 3 | 49.2 | 1300 | 49 (27) | 1/8 | 1550 | 240/208 | 926U20000KA |  |
|  | 480 | 1 | 42.6 | 1400 | 45 (25) | 1/6 | 1725 | 480 (1 ph) | 926U20000TA |  |
|  | 480 | 3 | 25 | 1400 | 45 (25) | 1/6 | 1725 | 480 (1ph) | 926U20000UA |  |
| 25 | 208 | 1 | 121.3 | 1300 | 61 (34) | 1/8 | 1550 | 240/208 | 926U25000CA |  |
|  | 208 | 3 | 70.5 | 1300 | 61 (34) | 1/8 | 1550 | 240/208 | 926U25000DA |  |
|  | 240 | 1 | 105.3 | 1300 | 61 (34) | 1/8 | 1550 | 240/208 | 926U25000JA |  |
|  | 240 | 3 | 61.2 | 1300 | 61 (34) | 1/8 | 1550 | 240/208 | 926U25000KA |  |
|  | 480 | 1 | 53 | 1400 | 56 (31) | 1/6 | 1725 | 480 (1 ph) | 926U25000TA |  |
|  | 480 | 3 | 31 | 1400 | 56 (31) | 1/6 | 1725 | 480 (1 ph) | 926U25000UA |  |
| 30 | 480 | 3 | 37 | 1400 | 68 (38) | 1/6 | 1725 | 480 (1 ph) | 926U30000UA |  |
| 40 | 480 | 3 | 49.6 | 2000 | 64 (18) | 3/4 | 1140 | 480 (3 ph) | 926U40000UA |  |
| 50 | 480 | 3 | 61.6 | 2000 | 80 (27) | 3/4 | 1140 | 480 (3 ph) | 926U50000UA |  |
| 60 | 480 | 3 | 73.7 | 2000 | 96 (36) | 3/4 | 1140 | 480 (3 ph) | 926U60000UA |  |

(1) Total Amps = Heating element amps and motor amps.

Other voltages available. Consult factory.

Only available with almond finish.

Factory Built-in Options

| Code | Description |  |
| --- | --- | --- |
| C | Three Pole Contactor |  |
| D1 | Disconnect Switch 40 Amp |  |
| D2 | Disconnect Switch 80 Amp (2) |  |
| D5 | Disconnect Switch (100 Amps maximum) |  |
| G | Fusing |  |
| M | Manual Reset |  |
| R1 | 24V Relay |  |
| R2 | 24V Relay with Transformer (1) |  |
| T | Thermostat (2) |  |
| U | Fan “ON” Switch |  |
| X | 120 V Control, fused secondary and grounded |  |

(1) Add option “R2” when low voltage remote thermostat is required.

(2) Not available with heater part number 926U10000CA.  Field-Installed Options

(shipped loose for field installation into heaters)

| Catalog Number | Description |  |
| --- | --- | --- |
| 926-124513 | Diffuser cone (2-10 KW) |  |
| 926-124514 | Diffuser cone (15-30 KW) |  |
| 926-161077 | Diffuser cone (40-60 KW) |  |
| 926-124515 | Thermostat Kit |  |
| 926-124516 | 24V Relay Kit |  |
| 926-124518 | 24V Relay Kit with Transformer |  |

Dimensions & Weight

| kW | A | B | C | D | E | F | G | H | I | Weight |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | in (mm) | in (mm) | in (mm) | in (mm) | in (mm) | in (mm) | in (mm) | in (mm) | in (mm) | lbs (kg) |
| 2-10 | 12 (305) | 16-1/2 (419) | 17 (432) | 14-1/16 (357) | 11-7/16 (290) | 19 (490) | 12 (305) | 4-7/8 (123) | 16-7/8 (428) | 45 (20) |
| 15-30 | 18 (444) | 21-7/8 (556) | 23 (572) | 19 (470) | 16 (407) | 25 (630) | 12 (305) | 5-13/16 (148) | 23-5/16 (592) | 85 (39) |
| 40-60 | 23 (585) | 25 (641) | 34 (870) | - | - | 36-3/8 (924) | 12 (305) | 12 (305) | 35 (890) | 150 (68) |

Ceiling Bracket	Wall Bracket 	4 Threaded Rods ½-13 UNC

Application

Small rooms may only require one unit heater (FIG #1) while other may require multiple unit heaters for proper perimeter circulation (FIG #2).

Architect’s and Engineer’s Specifications

The specified heating equipment shall include an electric, fan-forced air unit heater suitable for space heating as manufactured by INDEECO.  The commercial unit heater shall be designed for mounting in the vertical or horizontal position.  Heaters shall be third party approved to UL standard 2021.  CSA-US or equivalent is acceptable.

Heating Housing shall be made from 18 and 20 gauge steel.  Individual adjustable louvers with 30 degree downward stops shall be furnished to provide the desired control of discharge air.  Cabinet finish shall be an almond epoxy/polyester powder paint.  Mounting brackets designed for either ceiling or wall mounting shall be furnished as shown.  Housing shall include an outlet protective screen.  Screen shall prohibit debris from reaching the element compartment.

Heater Elements shall be located downstream of the motor and fan blade for uniform heating and to eliminate hot spots.

Fan and Motor shall be located upstream of heating elements.  This location allows the motor to run cooler and have a longer life expectancy.  The motor shall be thermally protected.

Fan Over-ride shall be included to purge the heater of residual heat when heater is de-energized.

Thermal Cutout shall be built-in to every heater and wired for instantaneous de-energizing of the heating elements.

Fusing shall be included when heater amperage exceeds 48 amps.  The fusing shall be factory installed and subdivided into circuits of 48 amps or less.  Fusing is optional for heater rated under 48 amps.

Thermostat is offered as an option.  Thermostat shall be built-in to heater and adjustable through main control compartment.  Standard control voltage is 240/208 with a transformer when necessary.  A 24 volt or 120 volt relay may be installed as an option.

Disconnect Switch is offered as an option up to 100 Amps.  The built-in disconnect switches is an inexpensive way to meet NEC/CEC requirements for a disconnecting means within sight of the heater.

Other Options include fan “ON” switch, 3 pole disconnecting contactor, relay/transformer kits for field installation or built-in to heater and diffuser cones for vertical airflow.

These units are not for residential use in the United States.

# Text boxes

40-60 kW

Support Brackets